## Slide 1: Data Transfer Node Performance GÉANT & AENEAS

## Slide 2: Agenda
Environment – HW and Topology
Tuning
UDP & TCP using the Kernel Stack
  Achievable UDP throughput vs packet spacing
  Achievable UDP throughput vs packet size
  Achievable TCP throughput and use of CPU cores, application, NIC ring buffer
  Achievable TCP throughput ConnectX-4 and ConnectX-5 – multiple flows
RDMA using the Kernel Stack
  RDMA RC Observed Protocol and Packet size
  RDMA RC throughput vs message size
  RDMA RC throughput vs packet spacing
Kernel bypass with libvma
  Achievable UDP throughput vs packet size
  Achievable UDP throughput vs packet spacing
  TCP throughput

## Slide 3: The GÉANT DTN Hardware
NIC
NVME
A lot of help from Boston Labs (London UK)
Mellanox (UK & Israel )
Supermicro X10DRT-i+ motherboard
Two 6 core 3.40GHz Xeon E5-2643 v3 processors,
Mellanox ConnectX-4/5 100 GE NIC
  16 lane PCI-e
  As many interrupts as cores
  Driver MLNX_OFED_LINUX-4.0-2.0.0.1
NVME SSD
  Set 8 lane PCI-e
Fedora 23 with the 4.4.6-300.fc23.x86_64 kernel
Notes: QPI Intel QuickPath Interconnect 9.6 GT/s
16 lane 32 GB/s

## Slide 4: DTN Topology 1
Back to Back, Active Cable, 100GBASE SR-4, 100GBASE LR-4
DTN Qualification in the GÉANT Lab
Juniper MX
Juniper MX

## Slide 5: DTN Topology 2
GÉANT DTNs in London & Paris AENEAS DTNs in Jodrell Bank

## Slide 6: Network Tuning for 100 Gigabit Ethernet
Hyper threading Turn OFF
Wait states Disable
Power saving Core Frequency Set governor “performance”
Set max CPU frequency
NUMA Select correct CPU cores
IRQs Turn off the irqbalance Use correct cores for NIC IRQs
Interface parameters Interrupt coalescence, Xsum offload, Ring buffer
MTU Set IP MTU 9000 Bytes
Queues Set txqueuelen, netdev_max_backlog
Kernel parameters r(w)mem_max, tcp_r(w)mem, tcp_mem, …
Firewalls
Better to choose fewer higher speed cores

## Slide 7: udpmon: UDP Achievable Throughput Ideal shape
Flat portions Limited by capacity of link
Available BW on a loaded link
Cannot send packets back-2-back
End host: NIC setup time on PCI / context switches
Shape follows 1/t
Packet spacing most important.

## Slide 8: udpmon: Achievable Throughput & Packet loss
Move IRQs from core 6, set affinity to lock udpmon to core 6 node 1.
Interrupt coalescence on (16us)
NIC: ConnectX-4
96% kernel sending
Swapping between user and kernel mode
37% kernel recv.
50 Gbit/s
Jumbo size packet should be highest !
Also lost packets in the receiving host
Notes: Recv CPU % idle ??

## Slide 9: udpmon_send: How fast can I transmit? Sending Rate as a Function of Packet Size
Move IRQs from core 6, set affinity to lock udpmon to core 6 node 1.
Step occurs 7813 – 7814 bytes user data
Step 0.29 µs
Drop 3.6 Gbit/s
Step 0.75 µs
Drop 14.5 Gbit/s from 43 Gbit/s
Collaborate with Mellanox
Not driver but the kernel
Notes: 50 ps / byte 8 bytes 0.4 ns/64 bits
Install and tested
Centos 7 kernel 3.10.0-327.el7.x86_64
Centos 6.7 kernel 2.6.32-573.e16.x86_64 Boston Labs OK

## Slide 10: udpmon: Size of Rx Ring Buffer
ConnectX-5, set affinity of udpmon to core 6 node 1.
Use ethtool -S <enp131s0f0> look at rx_out_of_buffer
RX ring 1024
RX ring ≥4096
To 8% packet loss
51 Gbit/s
No packet loss

## Slide 11: iperf3: TCP throughput and use of cores
Firewalls OFF, TCP offload on, TCP cubic stack
Rises smoothly to the plateau – except for the peak
Throughput 0.7MByte:
  80 Gbit/s both Send & Receive on node 1
  35 Gbit/s Send on node 0 Receive on node 1
  28 Gbit/s both Send & Receive on node 0
Very few TCP re-transmitted segments observed

## Slide 12: TCP Throughput iperf2 & iperf3
ConnectX-5, NIC rx buffer 4096, iperf Core6 – core6
While transmitting at 80 Gbit/s the CPU was 98% in kernel mode.
iperf3 iperf2

## Slide 13: TCP Throughput iperf2 effect of Rx Ring Buffer
ConnectX-5, iperf Core6 – core6
Correlation of low throughput and re-transmits for Rx ring 1024

## Slide 14: iperf: TCP throughput multiple flows
Distribute IRQs on node 1
Run iperf on cores 6-11 for both send & receive
Firewalls ON, TCP offload on, TCP cubic
Total throughput: increase 60  90 1  2 flows >95 Gbit/s for 3 & 4 flows
Re-transmission
  10-4 % 3 flows
  10-3 10-5 % 4 flows
  10-2 % 8, 10 flows

## Slide 15: Inside a RDMA Application
App design places Work Requests on Send Queue or Recv Queue
Need to check the Completion Queue – cannot over fill a Queue
Deal with low level memory allocation – like for NIC “ring buffers”
allocate
access
metadata
control
data packets
ACK
status
post_send()
USER
CHANNEL ADAPTER
WIRE
register
poll_cq()
send queue
completion queue
. . .
. . .
virtual
memory
Activity
blocked
Robert D. Russell
Notes: RoCE v2 UDP/ IP

## Slide 16: Inside a RDMA Application
Fill Recv Queue with Work Requests & ask for notification
Wait for event – packet arrival – then poll for status
Loop on RecvQ, use data, issue new Recv Work Request
Notes: RoCE v2 UDP/ IP

## Slide 17: RDMA RC
Max packet size 4096 Bytes,
Every message is acknowledged
Core6 – core6
the CPU was 90% in user mode.
App design takes care of ring buffers poll CompQ every 64 packets
Notes: RoCE v2 UDP/ IP

## Slide 18: RDMA RC Throughput as a function of msg size
Reasonably smooth increase with mssage size
~ 80 Gbit/s for Jumbo frame messages
>90 Gbit/s for 30k Byte messages
Not clear what small messages take so long.

## Slide 19: libvma user mode kernel bypass UDP Throughput as a function of msg size
Modify libvma to fragment correctly
  Fed back to Mellanox & into the distribution.
udpmon unmodified run core6 – core6
Firewalls ON
Smooth increase
UDP > 90 Gbit/s for Jumbo packets

## Slide 20: libvma UDP Performance
Core6 – core 6
Throughput >98 Gbit/s
No packet loss
Jitter excellent

## Slide 21: libvma TCP Performance
Core6 – core 6
TCP iperf kernel 57.7 Gbit/s
TCP iperf libvma 13.6 Gbit/s
libvma does not seem to trap iperf3 system calls.

## Slide 22: Questions ?
Thanks to Richard Hughes-Jones

## Slide 23: Progress & Status Task 4.1: Evaluation of existing data transfer protocols, storage sub-systems and applications
Test hosts set up at Onsala, JBO, GÉANT Cam & Lon, Jülich
Low-level protocol – end host measurements
  UDP, TCP, RDMA RoCEv2, kernel bypass libvma
Good performance with careful tuning single flows 60 – 95 Gbit/s
Technical Note started
Notes: Tests on local sites
Different hardware and OS versions

## Slide 24: iperf: TCP throughput multiple flows
Distribute IRQs over all cores on node 1
Run iperf on cores 6-11 for both receive and sending
Firewalls ON, TCP offload on, TCP cubic
Total throughput: increase 60  86 2  3 flows 98 Gbit/s for 4 & 5 flows then starts to fall
10-4 - 10-5 % re-tx 2, 3 flows
10-4 % re-tx 4, 5 flows
10-3 % re-tx 8, 10 flows
Individual flows can vary by ± 5 Gbit/s

## Slide 25: Network Tuning for 100 Gigabit Ethernet
Hyper threading
  Turn off in the BIOS
Wait states
  Disable / minimise use of c-states. Use the BIOS or at boot time Power saving Core Frequency
  Set governor “performance”
  Set cpufreq to maximum
  Depends on scaling_driver: acpi-cpufreq allows setting cpuinfo_cur_freq to max intel_pstate does not but seems fast anyway
NUMA
  Check and select CPU cores in the node with the Ethernet interfaces attached
$numactl –H
$cat /sys/devices/system/node/node*/cpulist
$lspci –tv
$cat /sys/class/net/*/device/uevent
Read the current settings
$cat /sys/devices/system/cpu/cpu*/cpufreq/*
$cat /sys/devices/system/cpu/cpu*/cpufreq/scaling_governor
Set
$echo “performance” > /sys/devices/system/cpu/cpu*/cpufreq/scaling_governor

## Slide 26: Network Tuning for 100 Gigabit Ethernet
IRQs
  Turn off the irqbalance service – prevents balancer from changing the affinity scheme.
  Set affinity of the NIC IRQs to use CPU cores on the node with PCIe
    1 per CPU.
    For UDP seems best NOT to use the CPU cores used by the apps.
Interface parameters
  Ensure interrupt coalescence is ON – 3 μs, 16 μs, more ?
  Ensure Rx & Tx checksum offload is ON
  Ensure tcp-segmentation-offload is ON
  Set the Tx Rx ring buffer size
MTU
  Set IP MTU 9000 Bytes
#cat /proc/irq/<irq>/smp_affinity
#echo 400 > /proc/irq/183/smp_affinity
#/usr/sbin/set_irq_affinity_cpulist.sh 8-11 enp131s0f0
#systemctl stop irqbalance.service
#ethtool –C <i/f> rx-usecs 8
#ethtool –K <i/f> rx on tx on
#ethtool –K <i/f> tso on
#ethtool –G <i/f> rx 8192
#ethtool –G <i/f> tx 8192
Best set in files eg ifcfg_ethx
mtu=9000

## Slide 27: Network Tuning for 100 Gigabit Ethernet
Queues
  Set txqueuelen – transmit Q (I used 1000 but 10,000 recommended)
  Set netdev_max_backlog – say 250000 – Q between interface and IP stack
Kernel parameters
  net.core.rmem_max net.core.wmem_max
  net.ipv4.tcp_rmem net.ipv4.tcp_wmem (min / default / max)
  net.ipv4.tcp_mtu_probing (jumbo frames)
  net.ipv4.tcp_congestion_control (htcp, cubic)
  net.ipv4.tcp_mem (set the max to cover rmem/wmem max)
Better to choose fewer high speed cores
  http://www.mellanox.com/related-docs/prod_software/Performance_Tuning_Guide_for_Mellanox_Network_Adapters.pdf
  Esnet FasterData https://fasterdata.es.net/network-tuning/
Best in file /etc/sysctl.conf
Notes:   Interface parameters – reduce CPU load